OIL RIG PLC MONITORING

& MOTOR CONTROL SYSTEM

Implementation & Deployment Guide

DVP-10SX PLC  →  USR-W630  →  Python Bridge  →  ThingsBoard CE

Prepared for: Oomnieye Digital Twin Solutions Pvt Ltd

Document version 1.0  |  August 2026

# Table of Contents

# 1. Project Overview

This system monitors a rig skid's environmental sensors (temperature, humidity, barometric pressure, gas resistance / air quality), wind speed and direction, and a 12V DC diaphragm pump motor (voltage, current, power, runtime), and exposes it all as live telemetry on a ThingsBoard dashboard. The same dashboard can also switch the motor ON/OFF remotely via an RPC command that is written back to the PLC.

A Delta DVP-10SX PLC is the field controller. It aggregates readings from an RS-485 environmental sensor (7Semi ENV-485: temperature/humidity/pressure/gas), an RS-485 anemometer, an analog current-amplifier + shunt (motor current), and an analog voltage sensor (motor voltage) into a contiguous block of Modbus holding registers. A USR-W630 serial-to-Ethernet converter exposes the PLC's RS-232 programming/Modbus port over TCP, which a Python script on a PC/gateway polls, converts to engineering units, and forwards to ThingsBoard over MQTT.

## 1.1 Key Capabilities

- Live environmental telemetry: temperature, humidity, pressure, gas resistance, derived IAQ index

- Wind speed and direction monitoring

- Motor voltage, current and computed power (P = V × I)

- Motor uptime, downtime and all-time cumulative runtime (persisted across restarts)

- Remote motor ON/OFF control from the ThingsBoard dashboard (RPC)

- Automatic stale-connection detection and Modbus TCP reconnect

- Standalone diagnostic tool for isolating sensor/link freeze issues

# 2. System Architecture

The diagram below shows the full signal and power chain from mains AC through to ThingsBoard.

Figure 1 — Overall block diagram (power, sensors, PLC, Modbus/RS-485 wiring)

## 2.1 Data Flow

- Sensors (ENV-485, anemometer) and analog modules (current amplifier, voltage sensor) feed the DVP-10SX PLC.

- PLC ladder logic mirrors all live values into holding registers 4096–4107.

- USR-W630 bridges the PLC's serial Modbus port to TCP/IP (Server mode, port 8899).

- oil_rig.py polls all 12 registers every 2 seconds over Modbus TCP (ASCII framer).

- Raw values are scaled into engineering units and derived fields are computed (power, flow rate, runtime, IAQ).

- The resulting JSON payload is published to ThingsBoard over MQTT as device telemetry.

- ThingsBoard dashboard widgets display telemetry and can send an RPC (setMotorState) back through the same script to switch the motor via a PLC register write.

# 3. Hardware Components

| Component | Role | Notes |
| --- | --- | --- |
| Delta DVP-10SX | Field PLC / register aggregator | 12V0 / A-D module, RS-485 port, C0/Y0 output drives motor |
| USR-W630 | RS-232 → TCP/IP converter | Server mode, TCP port 8899, connects to PLC programming/Modbus port |
| 7Semi ENV-485 | Temp / humidity / pressure / gas sensor | RS-485, registers confirmed against datasheet |
| Anemometer | Wind speed & direction | RS-485, shares bus with ENV-485 (yellow +, green −) |
| Current amplifier + shunt | Motor current sensing | Isolation amplifier, feeds PLC analog input channel |
| Voltage sensor module | Motor voltage sensing (±12V) | Feeds PLC analog input channel |
| TOPSFLO TM30A | 12V DC diaphragm pump (the “motor”) | Rated ~0.4A no-load; ~0.8–1A under load (estimated) |
| 12V SMPS | Motor / sensor 12V rail | 230V AC input |
| 24V DC 2.5A SMPS (60W) | PLC 24V rail | 230V AC input |

# 4. Wiring Reference

Use these two diagrams together with Circuit_Diagram_of_PLC.pdf (3-page EPLAN schematic) for the physical build or for verifying an existing installation.

Figure 2 — DVP-10SX pinout: A/D inputs (+CS, +VS, COM), 24V DC supply, RS-485 (yellow), C0/Y0 motor output

Figure 3 — Hand-marked wiring: SMPS, shunt polarity, current amplifier terminal numbers, voltage sensor, USR-W630

NOTE: Circuit_Diagram_of_PLC.pdf pages 1–3 contain the clean EPLAN version of the same wiring (power distribution, voltage sensor, current amplifier + shunt + motor) with cross-reference page/line numbers — use it as the authoritative reference when the hand sketches are ambiguous.

# 5. PLC Register Map

Base address 4096, 12 contiguous holding registers, read as one block on every poll cycle.

| Address (index) | Field | Scaling | Unit | Status |
| --- | --- | --- | --- | --- |
| 4096 (0) | temperature | raw / 100 | °C | Confirmed |
| 4097 (1) | humidity | raw / 100 | %RH | Confirmed |
| 4098-4099 (2,3) | pressure | (Hi<<16 ¦ Lo) / 100 | hPa | Confirmed |
| 4100-4101 (4,5) | gas_resistance | (Hi<<16 ¦ Lo) | Ohm | Confirmed |
| 4102 (6) | wind_speed | raw / 10 | m/s | Unconfirmed |
| 4103 (7) | wind_direction | 2=Right, 3=Left | - | Confirmed (rotation sense only) |
| 4104 (8) | motor_voltage | raw x 1 (whole volts) | V | Unconfirmed |
| 4105 (9) | motor_current | raw x 0.08 | A | Rescaled estimate |
| 4106 (10) | motor_power_plc_raw | raw x 1 | W | Diagnostics only, not used |
| 4107 (11) | motor_control | 0 / 1 | - | Also write address for ON/OFF |

CALIBRATION WARNING: Wind speed, motor voltage and motor current scale factors are not yet confirmed against a manufacturer datasheet or clamp-meter reading. CURRENT_SCALE (currently 0.08) in particular is a single-point estimate — recalibrate with a real clamp-meter reading under running load if accuracy matters for reporting.

# 6. Software Prerequisites

## 6.1 Requirements

- Python 3.8 or newer

- Network access from the PC/gateway to the USR-W630's IP on TCP port 8899

- A ThingsBoard CE instance and a device access token

## 6.2 Install Dependencies

pip install pymodbus paho-mqtt --break-system-packages
# (drop --break-system-packages on Windows / inside a venv)

# 7. Configuration

Open oil_rig.py and set the connection block at the top of the file before first run:

PLC_IP = "10.158.91.46"        # USR-W630 IP, Server mode, TCP
PLC_PORT = 8899
PLC_SLAVE_ID = 1

      
THINGSBOARD_HOST = "allcad-chennai.selfip.com"
THINGSBOARD_MQTT_PORT = 1883
THINGSBOARD_ACCESS_TOKEN = "<device access token>"

      
READ_INTERVAL_SEC = 2

NOTE: Do this once for a new deployment/device: confirm PLC_IP matches the USR-W630's configured static IP, and generate a fresh device access token in ThingsBoard (Devices → your device → Manage credentials) rather than reusing a token from another unit.

# 8. Step-by-Step Setup Procedure

- Wire the panel per Section 4 (Wiring Reference) and Circuit_Diagram_of_PLC.pdf. Double-check shunt polarity (+ve/−ve) and current-amplifier terminal numbers (5,6,7,8 input / 1,2 output) before powering on.

- Power up the 12V SMPS and 24V DC SMPS. Confirm the PLC's POWER and RUN LEDs are lit.

- Confirm PLC ladder logic mirrors ENV-485, anemometer, current-amplifier and voltage-sensor readings into holding registers 4096–4106, and that register 4107 accepts a motor ON/OFF write.

- Configure the USR-W630 as a TCP Server on port 8899, matching the PLC's serial port baud rate.

- On the gateway PC, verify network reachability: ping the USR-W630's IP, then confirm TCP port 8899 is open.

- Install Python dependencies (Section 6.2).

- Set PLC_IP, THINGSBOARD_HOST and THINGSBOARD_ACCESS_TOKEN in oil_rig.py (Section 7).

- Create the device in ThingsBoard and note its access token; add telemetry widgets for the keys listed in Section 9.2.

- Run: python oil_rig.py — confirm the console prints “Connected to PLC via USR-W630” and “Connected to ThingsBoard, rc = 0”.

- Watch the console telemetry print-out for 1–2 minutes and cross-check a couple of values (temperature, motor_voltage) against a known-good reference before trusting the feed.

- From the ThingsBoard dashboard, test the motor ON/OFF switch widget once and confirm the physical pump responds.

# 9. Running the System

## 9.1 Main Bridge — oil_rig.py

Run with: python oil_rig.py

- Loads any previously persisted motor_runtime_state.json on startup.

- Connects to the PLC over Modbus TCP and starts the ThingsBoard MQTT client on a background thread.

- Every READ_INTERVAL_SEC (default 2s): reads 12 registers, converts to engineering units, computes motor_power / flow_rate / uptime / downtime / total runtime / IAQ, and publishes to ThingsBoard.

- Listens for RPC calls (getValue, setMotorState) from the dashboard and writes motor ON/OFF back to register 4107.

- If the wind_speed register repeats an identical value for 10 consecutive reads, the script automatically closes and reopens the Modbus TCP connection.

- On exit (Ctrl+C), flushes the runtime counters to motor_runtime_state.json before closing connections.

## 9.2 ThingsBoard Telemetry Keys

| Key | Description |
| --- | --- |
| temperature, humidity, pressure, gas_resistance | Environmental readings |
| iaq_index, iaq_label | Derived air-quality score (0–500) and label |
| wind_speed, wind_direction, wind_direction_text | Anemometer readings |
| motor_voltage, motor_current, motor_power | Motor electrical telemetry |
| motor_control, flow_rate | Motor ON/OFF state and derived flow rate (L/min) |
| motor_uptime_min, motor_downtime_min, motor_total_running_min | Runtime counters |

## 9.3 Diagnostic Tool — wind_speed.py

Run with: python wind_speed.py

A safe, read-only tool that logs all 12 raw registers with timestamps to wind_speed_diagnostic_log.csv, without writing to the PLC or publishing to ThingsBoard. Run it alongside or instead of oil_rig.py for at least 15–30 minutes, ideally while conditions are actually changing (e.g. real wind blowing), then press Ctrl+C to print a per-register “% of reads changed” summary.

HOW TO READ THE SUMMARY: If a register changes on 0% of reads across a long run while others (e.g. motor_current) change normally, that register's source is not being refreshed — check the RS-485 wiring/PLC ladder logic for that sensor rather than the Python/TCP link. If ALL registers freeze together, or error_count climbs, suspect the USR-W630 ↔ PLC link instead.

# 10. Motor Runtime Tracking

motor_runtime_state.json stores a single field, total_running_sec, which persists cumulative pump runtime across script restarts, crashes and reboots. It is written roughly once a minute (every 30 reads at a 2-second interval) and flushed on clean shutdown.

{"total_running_sec": 2982.0}   // ≈ 49.7 minutes cumulative at last save

# 11. Troubleshooting

### 11.1 Registers appear frozen

Run wind_speed.py per Section 9.3. In prior diagnostic runs, every register except motor_current and motor_power_raw froze for the full session — this points to the RS-485/PLC refresh path (ENV-485, anemometer, voltage sensor mirroring) rather than the TCP link, since motor_current (fed through the current amplifier's own analog channel) kept changing normally throughout.

### 11.2 Modbus read errors / connection drops

- Confirm the USR-W630 is powered and its TCP Server is listening on the configured port.

- Check the framer setting (‘ascii’) matches the PLC's serial configuration.

- A high error_count in wind_speed.py's summary points to the USR-W630 ↔ PLC serial link rather than individual sensors.

### 11.3 Motor current / voltage look wrong

- motor_voltage and motor_current scale factors are estimates (Section 5) — recalibrate against a multimeter/clamp-meter reading taken while the pump is actually running under load.

### 11.4 ThingsBoard shows no telemetry

- Verify THINGSBOARD_ACCESS_TOKEN matches the device in ThingsBoard exactly.

- Confirm outbound MQTT (port 1883) isn't blocked by a firewall.

- Check the console for “Connected to ThingsBoard, rc = 0” — any non-zero rc indicates an auth or connection problem.

# 12. File Reference

| File | Purpose |
| --- | --- |
| oil_rig.py | Main PLC → ThingsBoard bridge (telemetry + RPC motor control) |
| wind_speed.py | Standalone read-only register diagnostic tool |
| motor_runtime_state.json | Persisted cumulative motor runtime |
| wind_speed_diagnostic_log.csv | Raw register log produced by wind_speed.py |
| overall_circuit.jpeg / Plc diagram.jpeg | Hand-marked wiring references |
| reference Diagram.png | Clean digital block diagram |
| Circuit_Diagram_of_PLC.pdf | 3-page EPLAN-style formal schematic |